## Slide 1: Pennsylvania Water Environment Federation PennTEC Annual Technical Conference June 4, 2013 Altoona Westerly Wastewater Treatment Facility BNR Conversion with Wet Weather Accommodation
Presented by:
Jim Balliet, Secretary/Facilities Planning Director
GWIN, DOBSON & FOREMAN, INC.
Consulting Engineers

## Slide 3: Westerly Treatment Facility
Originally constructed in 1952
Upstream 125 year old CSO System; “first flush” storage and pumping facility
Upgraded in 1990
  Coarse screening and aerated grit removal
  Complete mix activated sludge, single stage nitrification
  Final clarification and UV disinfection
  Equalization storage
Avg. Daily Flow – 10.8 mgd, Peak Flow – 60 mgd
Altoona Water Authority – System Owner/Operator

## Slide 4: The Chesapeake Bay Strategy
PA Dept. of Environmental Protection issued new NPDES permits to Altoona with mass annual nutrient load limits
Average effluent Nitrogen of 14.4 mg/l exceeds future cap load by 80,000 pounds, reduce N discharge by 45%
Average effluent Phosphorus of 3.0 mg/l exceeds future cap load by 15,000 pounds, reduce P discharge by 55%
Nutrient Cap Load Target Concentrations:
  Effluent Nitrogen – 5.0 mg/l
  Effluent Phosphorus – 0.67 mg/l

## Slide 5
Altoona
Notes: Distributing the Load
-what areas had most impact on Bay was a primary factor
-generally northern tribs have highest impact

## Slide 6: Project Goals
Reduce effluent nutrients levels to ensure regulatory compliance
Treat wet weather CSO flows while preventing washout of process nutrient biomass
Use sustainable design by maximizing use of existing facilities; reduce chemical consumption/waste solids
Reduce energy consumption using gravity flow, efficient NRT process
Reduce operating costs by using energy-efficient equipment and process monitoring & control system
Generate nutrient credits for sale on PA credit market

## Slide 7: Evaluation of Alternatives
Conducted extensive influent testing to characterize waste over full range of flows
Evaluated existing treatment processes and conducted preliminary screening of various Nutrient Removal Technologies (NRT)
BioWin process modeling of selected NRT processes with site-specific kinetic rates verified by High F/M testing
Evaluate wet weather CSO treatment options
Process evaluation by GDF and Bassett Engineering (process modeling and NRT consultant)

## Slide 8
Simulates biological processes of wastewater treatment plants
Developed By

## Slide 9: BioWin Model for NRT Process

## Slide 10: Selected Process
  Replace existing screens with fine screens.
  Replace aerated grit system with vortex grit separators
  Convert south EQ tank to two plug flow reactors.
  Convert existing aeration basins to two plug flow reactors.
  Construct fourth secondary clarifier.
  Provide chemical feed systems.
  Upgrade SCADA/instrumentation systems.

## Slide 11: Selected Process

## Slide 12: 1) Headworks building, 2) Primary Equalization Tanks, 3) Secondary Equalization Tanks 4) BNR Reactors 1 & 2, 5) BNR Reactors 3 & 4, 6) Final Clarifiers, 7) UV Units, 8) Aerobic Digesters, 9) Digested Solids EQ/Feed Tank, 10) Control Building and Sludge Handling
1
2
3
5
4
6
7
8
9
10

## Slide 13: Conversion of South Equalization Tank to NRT Reactors

## Slide 14: Selected Process
  Provide nutrient removal using four plug NRT reactors.
  Operational flexibility to operate various nutrient removal processes including Bardenpho, MLE, VIP, A20 and Hybrid
  Step feed high, diluted wet weather CSO flow to last oxic and swing zones to provide secondary (contact stabilization) treatment

## Slide 15
Chart: Westerly WWTF Typical Peak Flow Event (September 27 - October 7, 2011)

## Slide 16: Construction of Aeration Tanks Conversion, Distribution Box and Adjacent Step-Feed Channel

## Slide 17: Existing Aeration Tanks Converted to NRT Reactors and Adjacent Step-Feed Channel to Last Oxic Zone

## Slide 18: Hybrid BNR Feature
  Process combines the mixed liquor recycle feature from the VIP process with the Bardenpho process
  Mixed liquor from the final anoxic zone is recycled to the first anaerobic zone
  Lowers the oxidation/reduction potential (ORP) in the anaerobic zone
  Increases phosphorus release and enhances biological phosphorus removal
  Consistently meets P limits without chemical addition

## Slide 19: NRT Reactor

## Slide 20: Step Feed
  Diverts high wet weather CSO flow to last oxic zone
  Provides biological treatment of all CSO flows via contact stabilization (1-2 hour detention)
  Preserves treatment process sequence (anaerobic, anoxic and aerobic)
  Preserves nitrifiers and maintains N removal during and after high flow events
  Prevents elevated DO concentrations in process.
  Preserves solids washout in clarifiers

## Slide 21: Sustainable Design
  Converted existing aeration tank into two plug flow NRT reactors
  Converted existing equalization basin into two plug flow NRT reactors
  Existing tanks were retrofitted with baffle walls to create anaerobic, anoxic and aerobic zones
  Constructed slightly submerged walls with underflow ports
  Located recycle pumps in existing pipe gallery
  Reused air distribution piping, existing flow distribution channels, RAS piping and effluent channels

## Slide 22: Retrofitting of Existing Equalization Tank to NRT Reactor

## Slide 23: Pipe Gallery Tunnel with Internal Recycle & Air Piping

## Slide 24: Operational Flexibility
  Facility can operate in a variety of plug flow NRT removal modes (MLE, Stage 4/5 Bardenpho)
  Current operation uses Virginia Initiative Plant (VIP) process for step feeding wet weather flow
  Second anoxic zone is a switch zone (mixer and diffusers) and can operate as an oxic zone during step feed
  VIP process produces lower effluent N during cold weather without the second anoxic zone
  Internal RAS/MLSS/Nutrient recycle streams can draw and pump to multiple zones
  Wet weather CSO flow treated in contact stabilization mode in switch zone/last oxic zone

## Slide 25: Switch Zone – Membrane Diffusers (oxic) & Submersible Mixers (anoxic)

## Slide 26: BNR Initial Process Parameters
 | SRT | WAS | FM Ratio | MLSS | RAS | Total RAS | NR | MLR
 | (Days) | (MGD) | (per day) | (mg/L) | (mg/L) | (MGD) | (MGD) | (MGD)
Minimum | 2.25 | 0.07 | 0.04 | 1,835 | 3,700 | 2.60 | 1.60 | 0.90
Average | 6.20 | 0.18 | 0.11 | 3,420 | 8,680 | 6.20 | 3.75 | 2.00
Maximum | 14.50 | 0.34 | 0.33 | 4,880 | 11,950 | 8.30 | 4.70 | 2.50
September 2011 – February 2012

## Slide 27: VIP Process Operation During Wet Weather Flow

## Slide 28: VIP Process Operation During Wet Weather Flow

## Slide 29: Final Clarification
  Project included the addition of a fourth clarifier and upgrades to existing three clarifiers
  Surface overflow rate adequate for 60 mgd peak
  Employed rapid sludge removal via spiral blade sludge collectors
  Full radius skimmers
  Current density baffles (Stamford-type)
  Sludge blanket density meters

## Slide 30: Final Clarifiers with Stamford Baffles

## Slide 31: SCADA Process Control Features
  Step-feed process flow control
  Mixed liquor and nitrate recycle return rate
  RAS and WAS return rates
  DO control of air supply valves and blower speeds
  NO₄ control of nitrate recycle pumps and methanol
  RP control of mixed liquor recycle
  pH control of caustic soda feed
  NH₄ and PO₄ instruments provide process alarms

## Slide 32: Other Facility Improvements
  Fine Screening
  Non-Aerated Vortex Grit Separation
  Final Clarifier Additions and Upgrades
  Ultraviolet Disinfection System
  Aerobic Digester System Upgrades
  Effluent Screw Lift Pumps

## Slide 33: New Headworks Building

## Slide 34: Headworks Fine Screening

## Slide 35: Vortex Grit Separation System (preserve influent carbon)

## Slide 36: Ultraviolet Disinfection System

## Slide 37: Centrifuge Sludge Dewatering System

## Slide 38: 60” Diameter Screw Lift Flood Pumps

## Slide 39: Energy Efficient Turbo Blowers (high turndown capability)

## Slide 40: Chemical Feed and Storage Facilities

## Slide 41: Internal Recycle Pumps – Mixed Liquor & Nitrate

## Slide 42: BNR Process Results
  Process reduced effluent nitrogen concentration to near 3.0 mg/l with NO CARBON ADDITION
  Reduced annual N loading from 240,000 pounds to 70,000 pounds
  Biologically reduced annual P loading from 32,000 to 6,700 pounds with NO CHEMICAL ADDITION
  Generated $217,000 in nutrient credit revenue
  Processed 100% OF WET WEATHER FLOW WITHIN PERMIT LIMITS WITHOUT BNR PROCESS UPSET
  Annual plant operating costs REDUCED BY $110,000

## Slide 43
Chart: BNR Process - Effluent Flow, BOD, TSS, and Ammonia

## Slide 44
Chart: Westerly WWTF BNR Process - Effluent TKN, NOx-N, TN, and TP
| 40812 | 40815 | 40818 | 40821 | 40824 | 40830 | 40833 | 40836 | 40839 | 40842 | 40845 | 40848 | 40851 | 40854 | 40857 | 40860 | 40863 | 40866 | 40869 | 40872 | 40875 | 40878 | 40881 | 40884 | 40887 | 40890 | 40893 | 40896 | 40899 | 40902 | 40905 | 40908 | 40911 | 40914 | 40917 | 40920 | 40923 | 40926 | 40929 | 40932 | 40935 | 40938
Effluent TN | 4.02 | 2.21 | 2.42 | 1.72 | 2 | 1.6987 | 1.7111 | 1.8541 | 2.04 | 2.2 | 2.7966 | 2.5888 | 2.383 | 2.511 | 1.8327 | 2.5499 | 2.5 | 2.24 | 2.15 | 2.513 | 2.1378 | 1.92 | 2.188 | 2.991 | 1.807 | 2.282 | 2.3532 | 3.0546 | 2.1269 | 2.8661 | 3.6617 | 2.872 | 3.0517 | 2.7316 | 3.1675 | 3.3229 | 3.8242 | 3.3534 | 2.87 | 3.1789 | 3.161 | 3.2289
TN Goal | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Effluent TKN | 2.32 | 1.21 | 1.42 | 1 | 1 | 1.15 | 1 | 1.1 | 1.26 | 1 | 1.32 | 1 | 1 | 1 | 1 | 1 | 1.07 | 1 | 1.17 | 1.41 | 1 | 1 | 1 | 2.19 | 1 | 1 | 1 | 1.28 | 1.04 | 1.26 | 1.67 | 1 | 1.09 | 1 | 1.335 | 1.685 | 1.82 | 1.66 | 1.37 | 2.04 | 2 | 2
Effluent NOx-N | 1.7 | 1 | 1 | 0.72 | 1 | 0.5487 | 0.7111 | 0.7541 | 0.78 | 1.2 | 1.4766 | 1.5888 | 1.383 | 1.511 | 0.8327 | 1.5499 | 1.43 | 1.24 | 0.98 | 1.103 | 1.1378 | 0.92 | 1.188 | 0.801 | 0.807 | 1.282 | 1.3532 | 1.7746 | 1.0869 | 1.6061 | 1.9917 | 1.872 | 1.9617 | 1.7316 | 1.8325 | 1.6379 | 2.0042 | 1.6934 | 1.5 | 1.1389 | 1.161 | 1.2289
Effluent TP | 0.92 | 0.55 | 0.36 | 0.06 | 0.07 | 0.1 | 0.09 | 0.19 | 0.19 | 0.13 | 0.96 | 0.59 | 0.99 | 1.06 | 0.25 | 0.11 | 0.46 | 0.83 | 1.1 | 0.25 | 0.1 | 0.22 | 0.05 | 0.39 | 0.09 | 0.08 | 0.06 | 0.08 | 0.1 | 0.1 | 0.22 | 0.05 | 0.14 | 0.52 | 0.12 | 0.21 | 0.24 | 0.22 | 0.09 | 0.37 | 0.27 | 0.25
TP Goal | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67 | 0.67

## Slide 45
Chart: Total Effluent Nitrogen Concentration
| 40452 | 40483 | 40513 | 40544 | 40575 | 40603 | 40634 | 40664 | 40695 | 40725 | 40756 | 40787 | 40817 | 40848 | 40878 | 40909 | 40940 | 40969 | 41000 | 41030 | 41061 | 41091 | 41122 | 41153
 | 11.6347 | 9.6656 | 9.2684 | 12.5602 | 7.875 | 5.5834 | 5.6889 | 6.7234 | 10.5085 | 15.0654 | 8.7552 | 4.6409 | 2.2434 | 2.291 | 2.7576 | 3.295 | 3.7485 | 2.8251 | 4.3088 | 2.9277 | 3.3258 | 3.6809 | 3.006 | 3.0231
 | 0 | 20

## Slide 47
Chart: Annual Total Nitrogen Effluent Loading
| Oct 07 - Sep 08 | Oct 08 - Sep 09 | Oct 09 - Sep 10 | Oct 10 - Sep 11 | Sep 11 - Oct 12
Total Nitrogen (TN) | 214864 | 206064 | 214621 | 241373 | 60281
TN Cap Limit (164,381) | 164381 | 164381 | 164381 | 164381 | 164381

## Slide 48
Chart: Annual Total Phosphorus Effluent Loading
| Oct 07 - Sep 08 | Oct 08 - Sep 09 | Oct 09 - Sep 10 | Oct 10 - Sep 11 | Sep 11 - Oct 12
Total Phosphorus (TP) | 32779 | 28240 | 32133 | 29519 | 9524
TP Cap Limit (21,918) | 21918 | 21918 | 21918 | 21918 | 21918

## Slide 49
Chart: Westerly WWTF - Monthly Average O&M Costs
| Lab Cost & Supplies | Electricity | Chemicals | Maintenance (Plant) | Maintenance (CSO) | Sludge Disposal | Natural Oil & Gas
Oct 2010 - Sep 2011 | 4971.0292 | 32089.8192 | 3088.9008 | 6990.155 | 1115.22 | 3804.4992 | 3987.1567
Oct 2011 - Sep 2012 | 3112.7725 | 28288.9583 | 2466.4508 | 7463.0775 | 266.8142 | 1905.4075 | 3272.0892

## Slide 52: Questions/Discussion